Industrial Cooling Water Treatment — Domain Primer and Dataset Guide

Part 1. The domain

1.1 What a cooling system does

A cooling system takes heat from process equipment (heat exchangers, condensers) and rejects it to the environment.

Open recirculating system. Water circulates in a closed loop between the process heat exchangers and a cooling tower. In the tower, the hot water is distributed over fill and contacted with an air stream. Most of the heat is rejected by evaporating a small fraction of the water; the rest goes by sensible heat transfer. The cooled water returns to the process.

Because only pure water evaporates, all dissolved salts stay behind and concentrate in the loop. This is the single fact that generates the entire chemistry problem.

Basic streams and parameters

| Symbol | Meaning |
| --- | --- |
| t_hot | temperature of the water returning from the process, entering the tower |
| t_cold | temperature of the water leaving the tower basin, going to the process |
| RR | recirculation rate — total water flow through the loop |
| MU | makeup — fresh water entering the system |
| BD | blowdown — all water leaving the system in liquid form |
| E | evaporation — water leaving in vapour form |
| Heat load | heat rejected to the environment |

Blowdown has three components, and only the first one is metered:

- controlled blowdown — a valve, deliberately opened to keep salinity down;

- uncontrolled blowdown — leaks;

- drift — droplets carried out with the air stream past the demister.

Core equations

Heat load:

Q = Cp *  (T_hot - T_cold) * RR

Evaporation (simple engineering correlation; a rigorous value comes from Poppe theory):

E = (0.575 + 0.011 * Tair) * (T_hot- T_cold) * RR/580

Water balance:

MU = E + BD

Cycles of concentration — how many times the makeup salinity has been concentrated in the loop:

cycles =MU/BD

Salt balance, where C is concentration and Retention is the fraction of an ion that actually leaves in the blowdown rather than depositing in the system:

MU * C_MU = BD * C_RR * Retention

If retention is 100 % for a given ion, cycles can equivalently be obtained from chemistry:

cycles = MU/BD = C_RR/C_MU

Practical note on which method to trust. Cycles computed from flows is the honest number, but   BD is often poorly known. Cycles computed from chemistry requires an ion that is truly conservative. Chloride is the usual choice — but not when sodium hypochlorite is dosed, because that introduces a second chloride source. Silica is usually conservative; calcium and alkalinity are not, because they precipitate. In practice the best route is: compute E from the correlation, get BD from the water balance, and cross-check against a conservative ion.

Comparing cycles-by-flow against cycles-by-ion is itself a measurement: retention < 1 means the ion is being lost to scale.

Holding time index — the time needed to replace half the water in the system:

$$HTI =ln 2*V/BD

Below ~24 h, water chemistry is hard to hold: one dosing-pump stoppage and the inhibitor residual collapses. Above ~100 h, water sits in the system long enough that some chemicals degrade and lose performance.

1.2 Judging cooling tower performance

ΔT = t_hot − t_cold is often mistaken for an efficiency measure. It is not, because two devices are in series. The tower cannot reject more heat than the process delivers. But if the tower performs badly, t_cold rises, the heat exchangers transfer less, and ΔT falls. So a low ΔT is ambiguous: it may mean a tower problem, or simply a lower process heat load. The two cases must be separated using external information (weather, process load).

The proper measure uses the wet-bulb temperature T_wb, which is the thermodynamic floor for t_cold. T_wb is computed from air temperature, humidity and pressure (the CoolProp library does this).

- Approach = t_cold − T_wb. Typical summer values: 3–7 °C.

- Effectiveness = $\dfrac{T_{hot} - T_{cold}}{T_{hot} - T_{wb}}$. Typical summer values: 60–80 %.

A more fundamental description is the NTU of the tower (Merkel, or the more advanced Poppe method), which depends on the L/G ratio — kg of water per kg of dry air through the tower.

NTU = C * LG^(n)

n – is more or less stable value, C - characteristic of filling of cooling tower. When cooling tower is fouled, C decreases

1.3 Judging heat exchanger performance

Q = U * A * LMTD

LMTD = (Delta T_2 - \Delta T_1)/(ln(Delta T_2 / Delta T_1)

where Delta T_1, Delta T_2 are the hot/cold stream temperature differences at the two ends of the exchanger, A is the heat transfer area and U the overall heat transfer coefficient.

One cooling loop typically serves many heat exchangers, and usually not all of them are instrumented. But wherever temperatures and water flow are known, Q and LMTD follow, and therefore U·A. Since A is fixed, the trend of U·A over time is a direct measure of how clean the exchanger is. A steady decline is fouling or scaling. This is one of the most valuable derived signals in the whole domain.

1.4 What goes wrong

- Corrosion. Carbon steel, copper and stainless steel oxidise in water. Beyond the equipment damage, the corrosion products themselves foul heat exchangers, and dissolved iron degrades scale-inhibitor performance. So corrosion feeds back into the other failure modes.

- Scale. Minerals dissolved in the makeup water become insoluble under loop conditions (higher concentration, higher skin temperature) and deposit on heat transfer surfaces.

- Fouling. Insoluble solids from the makeup water, corrosion products and oil leaks accumulate in exchangers.

- Biological activity. Bacteria - the sessile ones forming biofilm, not the planktonic ones floating in the bulk water - create biofouling, which in turn accelerates both scale and corrosion.

These four are coupled, which is why single-variable models tend to disappoint.

1.5 Treatment chemicals and their dosing logic

The dosing basis differs by chemical type, and this matters for feature engineering -  a kg/day figure means different things for different products.

- Scale and corrosion inhibitors — inorganic phosphates, organophosphates, zinc, or film-forming compounds. Dosed proportionally to blowdown; the control target is a constant measured residual in the loop.

- Dispersants -  keep foulants suspended. Dosed on blowdown or makeup, either continuously or as slug doses.

- Biocides:

  - Non-oxidising (organic). Bacteria can develop tolerance, so these are dosed periodically as slugs, sized on system volume, aiming to reach a kill concentration for a contact time.

  - Oxidising (hypochlorite, chlorine dioxide, hydrogen peroxide). Dosed continuously against recirculation rate to hold an active residual; if slug-dosed, the target is an active residual sustained for a defined time.

1.6 Laboratory analysis and indices

Both makeup and recirculating water are monitored: pH, conductivity, suspended solids, oil, calcium, alkalinity, iron, hardness, chloride, sulphate, orthophosphate, inorganic phosphate, total phosphate.

Phosphate bookkeeping, which is a frequent source of confusion:

total phosphate     = organic phosphate + inorganic phosphate

inorganic phosphate = orthophosphate + condensed inorganic phosphate

Organic phosphate is normally the scale inhibitor residual; orthophosphate is normally the corrosion inhibitor. That is what makes these columns behave as a dose-response signal rather than as a raw water property.

Two derived indicators:

- Corrosivity of the water ≈ (chloride + sulphate) / alkalinity.

- Scaling tendency — Langelier or Ryznar index, or proper saturation indices from a speciation code such as PHREEQC or Reaktoro.

An important correction to the textbook reading. It is widely written that LSI > 0.5 means scale will form. That is wrong in a treated system. Every scale inhibitor, on a given system, can hold a certain level of supersaturation without deposition. For calcium carbonate with HEDP/ATMP-based inhibitors, a saturation index around 2 is routinely held stable. So the saturation index is not a threshold classifier — it is a continuous stress variable whose tolerable ceiling is itself a property of the treatment program. Recovering that ceiling from data is one of the interesting modelling questions here.

Part 2. The dataset

2.1 Scope and conventions

One plant, one open recirculating cooling loop, tagged S2CT2 (cooling tower 2 of unit S2). The S2CT2 tag exists because the same schema is used for several towers at the site; only this one is included here.

- Every table is keyed on rdate (timestamp). This is the only join key.

- Sampling frequency differs per table (see below). Nothing is aligned yet.

- Units, unless stated otherwise:

  - ec — µS/cm; tds — ppm (usually computed as ec × k, not measured)

  - ca_caco3 — ppm as CaCO₃

  - alk — meq/L. Multiply by 50 to get ppm as CaCO₃. This is the single most common mistake when working with this data.

  - phosphates — ppm as PO₄

  - fe, tss, oil — ppm; tvc — CFU/mL

  - flows — m³/h; temperatures — °C

  - dosages — kg/day of commercial product as supplied, not active matter

2.2 Files

tech_b2s2.xlsx — sheet S2CT2 (operational data)

432 daily rows, 2025-07-01 → 2026-09-05. This is the process backbone.

| Column | Meaning |
| --- | --- |
| t_cold | recirculating water temperature after the tower (to process) |
| t_hot | recirculating water temperature before the tower (from process) |
| ec_mu | makeup water conductivity, from an online sensor |
| mu | makeup flow |
| bd_c | controlled blowdown flow |
| rr_c1, rr_c2 | recirculation rate, tower cell 1 and cell 2 |

Total recirculation is rr_c1 + rr_c2 (≈ 3400 m³/h), not either column alone. I verified this against the water balance: with the summed flow, mean evaporation comes to ≈ 14.6 m³/h and E + bd_c ≈ 20.2 m³/h against a measured makeup of 23.3 m³/h. The ~3 m³/h gap is the unmetered part — leaks and drift — which is a physically sensible magnitude. With only one cell the balance does not close at all. The sheet abbr in this file carries the same definitions.

rr_analysis.xlsx (recirculating water chemistry)

- Sheet S2CT2 — 1358 rows, 2021-07-19 → 2026-08-05. The longest history in the dataset. Irregular sampling: a few times per week for the routine parameters, much rarer for others.

- Sheet MU — 177 rows, 2021-07 → 2022-08. Makeup chemistry for the old period only. It does not overlap with mu_water.xlsx; together they give a makeup record with a multi-year hole in the middle.

Columns: ph, ec, tds, ca_caco3, alk, cl, fe, tss, oil, tvc, po4_orto, po4_org, po4_tot plus three already-derived columns: lsi, cycles_tds, cycles_ca, retention_ca.

Fill rates are very uneven — roughly 530/1358 rows for pH and conductivity, 258 for iron, 49 for chloride. Treat sparsity as informative: routine daily parameters versus occasional special campaigns.

mu_water.xlsx — sheet analysis (makeup water chemistry)

281 rows, 2025-08-04 → 2026-08-17, timestamped to the hour. Same parameter set, plus toc, cod (both entirely empty) and operator_name (Cyrillic text — useful for detecting operator-dependent measurement bias). Only ~109 rows carry the main chemistry; the remaining rows are single-parameter entries. Sheet abbr holds the parameter dictionary.

corrosion.xlsx — sheet S2CT2

66 monthly rows, 2021-01 → 2026-07. Column corrosion is the corrosion rate in mm/year, from weight-loss coupons exposed for roughly one month, plus type (coupon metallurgy) and supplier — 60 of 66 rows carry these.

This is the main hard target, and it is the scarcest data in the set: one integrated value per month, so a coupon result is a month-long average, not a point measurement. Any model must respect that time support.

dosage_sched_june / july / august .xlsx — sheet S2CT2

Daily dosage in kg/day of commercial product, June–August 2026 only (30 + 31 + 31 rows). Same 11 columns in each file; Abbr sheet gives the key. Active-matter content is stated there and must be applied:

| Column | Product | Note |
| --- | --- | --- |
| h3po4_85 | phosphoric acid 85 % | yields 82 % as orthophosphate |
| pbtc_50 | PBTC 50 % — scale inhibitor | yields 15 % as organic phosphate |
| th3100 | TH-3100, 42 % AA/AMPS | polymeric dispersant |
| pg | polyglycol — biodispersant | a poor product choice, kept for honesty |
| cmitmit | CMIT/MIT 14 % | non-oxidising biocide |
| dbnpa | DBNPA, solid | non-oxidising biocide |
| peg | polyethylene glycol | solvent for DBNPA, not an active |
| ddac_50 | quaternary amine 50 % | non-oxidising biocide |
| js67, js68 | commercial CMIT/MIT blends |  |
| naclo | sodium hypochlorite | oxidising biocide |

The June file also contains two raw operator log sheets (350, 800, in Russian) and an empty Лист1 — ignore them, the S2CT2 sheet is the cleaned version.

To turn kg/day into something comparable with a measured residual: ppm ≈ kg/day × active_fraction × 1000 / (flow_m3/h × 24), using blowdown flow for inhibitors and recirculation for oxidising biocide, per §1.5.

weather_raw.xlsx — sheet nizhnekamsk_20250801_20260816

3045 rows at a 3-hour step, 2025-08-01 → 2026-08-16. Scraped, and it shows:

- rdate is text in DD.MM.YYYY HH:MM format, sorted descending. Parse with an explicit format string, or pandas will silently mangle the day/month order.

- temp — air temperature, °C (range −29.6 to +34.8; this is a continental climate, which is why seasonality dominates almost everything)

- P — barometric pressure in mmHg; U — relative humidity in %

- press, humidity — the same two values converted to Pa and fraction, and they are stored as Excel formulas. Read with data_only=True to get the cached numbers, or just recompute from P and U.

These are the inputs for wet-bulb temperature, and therefore for tower approach and effectiveness.

main.ipynb, pixi.toml, pixi.lock

Working notebook and a reproducible environment (pixi, conda-forge, Python 3.14: pandas, scipy, matplotlib, openpyxl, reaktoro, phreeqpython). The notebook contains the current hand-rolled approach: Langelier and phosphate saturation index functions, an empirical pH = a + b·log10(alkalinity) fit, cycles computed both from calcium ratio and from a TDS/calcium correction, and a comparison of empirically measured CCPP against Reaktoro/PHREEQC predictions. It is a starting point, not a finished pipeline.

2.3 Data quality issues — read before modelling

- Different time supports. Operations are daily, chemistry irregular (2–3× per week), weather 3-hourly, corrosion monthly. Everything must be resampled to a common grid; weekly is usually the practical compromise, and monthly is forced whenever corrosion is the target.

- Different date ranges. Loop chemistry goes back to 2021; operational and weather data start mid-2025; dosage exists only for three months of 2026. The fully-joined window is therefore narrow. Design around this: either accept ~3 months of complete records, or model in stages with different feature sets per stage.

- Derived columns already present. lsi, cycles_tds, cycles_ca, retention_ca in rr_analysis are computed from other columns in the same row. Using them as features to predict their own inputs will leak. Worse, some were computed with earlier and slightly different formulas, so they are not perfectly consistent with a fresh recomputation. Recompute from raw.

- Sensor artefacts in tech_b2s2. mu and bd_c both contain zeros and near-zeros (bd_c even goes slightly negative), with maxima of 117 and 83 m³/h against medians of 22 and 4.9. These are outages and flushes, not physics. Cycles computed naively as mu / bd_c explodes. Filter, or better, derive blowdown from the evaporation balance.

- tds is not measured, it is ec × k. It carries no information beyond conductivity; do not treat the two as independent features.

- Alkalinity units. meq/L in the chemistry tables, ppm as CaCO₃ in every formula in Part 1. Factor of 50.

- Manual laboratory data. Expect operator effects, transcription errors and rounding. operator_name in mu_water.xlsx lets you test for it.

Part 3. What is worth predicting

Roughly in order of business value against data availability.

- Corrosion rate. The direct target — corrosion.xlsx. Hard mode: 66 monthly points, so a general-purpose model will overfit instantly. This is a place for a physically-structured model with few parameters (corrosivity ratio, inhibitor residual, temperature, iron, TVC) rather than a flexible learner.

- Heat exchanger fouling. Track U·A over time per §1.3 and forecast the decline to schedule cleaning. Needs exchanger-side temperatures, which are not yet in this dataset - worth discussing whether they can be exported.

- Scaling / calcium retention. retention_ca < 1 quantifies calcium disappearing into scale. Relating it to saturation index, temperature and inhibitor residual would let us recover the inhibitor's tolerable supersaturation ceiling empirically, per §1.6. This is the most scientifically interesting question in the set. But here retention can be not very good parameter, it is something like > 1.0 for a long time, but according to information from the plant they have some problems

- Inhibitor residual as a soft sensor. Predict po4_org and po4_orto from the dosage files plus blowdown, and flag the residual between prediction and lab result. Deviations mean pump failures, inhibitor consumption by deposition, or degradation. Limited to the 3-month dosage window for now.

- Cooling tower performance. Approach and effectiveness from weather. Degradation shows up as a rising approach at constant wet bulb — this separates a fouled tower from a low process load, resolving the ΔT ambiguity of §1.2.

- Water balance validation. Continuously reconcile MU = E + BD and flag growing discrepancy as unmetered loss (leaks, drift). Cheap to build, immediately useful, and it doubles as a data quality monitor for everything above.

Physical constraints worth building into the models rather than learning from scratch: the mass balance, the salt balance, the evaporation correlation, and the monotonicity of saturation indices in temperature and concentration. The dataset is too small to rediscover these, and they hold exactly.